Equipment Type		Range of Fire-Retardant or Heat-Resistant Protection
1. Indoor (outdoor) hydrant and water-jet equipment	Operating indicator light / Emergency power supply / Control Panel or receiver of fire alarm equipment / Motor Pump / Operating device / Fire hydrant house
Automatic sprinkler, water spray, foam water spray, and cooling sprinkler systems	Supplementary sprinkler hydrant operating indicator light / Remote control switch / Alarm / Emergency power supply / Control Panel or receiver of / fire alarm equipment / Motor Pump / Pressure detector / Water flow detector
Carbon dioxide and dry chemical extinguishing systems	Release light / Emergency power supply / Control Panel / Detector / Automatic shut-off device / Power “On” Switch / Solenoid valve / Gas containers for system activation purpose / Storage containers / Exhaust device / Sound alarms
Automatic fire alarm system	Repeater / Note 2 / Note 1 / Note 1 / Note 3 / Emergency power supply / Receiver of fire alarm equipment / Fire alarm bell / Indicator light / Fire safety equipment operating circuit / Detector / Detector / Fire manual station / Addressable Fire manual station / Addressable detector / Addressable detector
Automatic gas leakage detecting fire alarm system	Detector / Detector / Note 2 / Note 3 / Emergency power supply / Remote operating device / Amplifier operating system operating systemIndicator light / Receiver of fire alarm equipment / speaker / Repeater / Alarm system of detection zone / Gas leakage indicator light
Emergency broadcasting system	Amplifier / Speaker / Emergency power supply / Indicator light / Operating device (including the remote operating device) or activating device
Signs of exit and direction system	Note 4 / Note 4 / Emergency power supply / Direction light / Exit light
Emergency lighting equipment	Emergency power supply / Emergency light / Note 5
Standpipes and dedicated firefighting water reservoir	Emergency power supply / Control panel or receiver of fire alarm equipment / Operating divice / Motor Pump / Operating indicator light / Hose connection or water supply connection
Smoke exhaust equipment	Note 6 / Emergency power supply / Control panel or receiver offFire alarm equipment / Detector / Motor Smoke exhaust fan / Smoke exhaust vent / Manual station or remote operating device
Emergency power supply sockets	Emergency power supply / Indicator light / Emergency power supply socket
Auxiliary wireless tele- / communication equipment	Emergency power supply / leaky coaxial cable / Amplifier / Radio signal connector / Distributor / leaky coaxial cable / Antenna
Note 1: Where the fire manual station also serves as an operation device for other fire safety equipment, the fire manual station and the indicator light circuitry shall be heat-resistant. / Note 2: The repeater (also referred as the module) emergency power circuit: Where the repeater contains built-in batteries, regular wiring shall be permitted. / Note 3: The repeater control circuit shall be permitted to be heat-resistant. / Note 4: Where sign systems contain built-in batteries, regular wiring shall be permitted. / Note 5: Where incombustible construction materials are used for ceiling and base panel, heat-resistant protection shall be permitted. Where the emergency lights contain built-in batteries, regular wiring shall be permitted. / Note 6: Where an external emergency power source is necessary to keep vents in opening condition after being opened, the emergency power supply circuit shall be flame-retardant.
Remarks: 1. Devices obtaining emergency power from the receiver of fire alarm equipment or control panel shall be flame-retardant; the control circuits thereof shall be heat-resistant. / 2. The wiring connecting the monitoring or operating devices of the Disaster Prevention Center to the fire safety equipment shall be heat-resistant. The wiring connecting said monitoring or operating devices to the emergency power supply shall be flame-retardant. However, where the receiver of fire alarm equipment, amplifier, and operating devices are installed inside the Disaster Prevention Center, regular wiring shall be permitted for the wiring within the center premises / 3. : flame-retardant; : heat-resistant; : coaxial cable; : regular wiring; : pipes